## sheet1
Version 2 | Время основе
Comment | Address mode | Interval | No. of data | Active only when designated window opened | PLC Name (Source) | Device Type (Source) | System Tag (Source) | User-defined Tag (Source) | Address (Source) | Index (Source) | PLC Name (Destination) | Device Type (Destination) | System Tag (Destination) | User-defined Tag (Destination) | Address (Destination) | Index (Destination) | Notification enable | Notification mode | Notification follow | PLC Name (Notification) | Device Type (Notification) | System Tag (Notification) | User-defined Tag (Notification) | Address (Notification) | Index (Notification) | Security interlock enable | Condition | PLC Name (Interlock) | Device Type (Interlock) | System Tag (Interlock) | User-defined Tag (Interlock) | Address (Interlock) | Index (Interlock) | Priority
чтение АКБ | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10342 | IDX: null | Local HMI | DG_read_AKK | System Tag: Off | User-defined Tag: On | LW-0 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение RPM | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10377 | IDX: null | Local HMI | DG_read_RPM | System Tag: Off | User-defined Tag: On | 1 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение температуры и давления | 1 | 10 | 2 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10362 | IDX: null | Local HMI | DG_read_Pressure | System Tag: Off | User-defined Tag: On | 3 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение мощности | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10295 | IDX: null | Local HMI | DG_read_active_Power | System Tag: Off | User-defined Tag: On | LW-5 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L1, V | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10247 | IDX: null | Local HMI | DG_read_voltage_L1 | System Tag: Off | User-defined Tag: On | LW-6 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L2, V | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10249 | IDX: null | Local HMI | DG_read_voltage_L2 | System Tag: Off | User-defined Tag: On | LW-8 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L3, V | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10251 | IDX: null | Local HMI | DG_read_voltage_L3 | System Tag: Off | User-defined Tag: On | LW-10 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L1, A | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10271 | IDX: null | Local HMI | DG_read_current_L1 | System Tag: Off | User-defined Tag: On | LW-12 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L2, A | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10273 | IDX: null | Local HMI | DG_read_current_L2 | System Tag: Off | User-defined Tag: On | LW-14 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение L3, A | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10275 | IDX: null | Local HMI | DG_read_current_L3 | System Tag: Off | User-defined Tag: On | LW-16 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение Q, кВар | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10311 | IDX: null | Local HMI | DG_read_Q | System Tag: Off | User-defined Tag: On | LW-18 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение S, кВА | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10327 | IDX: null | Local HMI | DG_read_S | System Tag: Off | User-defined Tag: On | LW-20 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение cos φ | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10336 | IDX: null | Local HMI | DG_read_cos | System Tag: Off | User-defined Tag: On | LW-22 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтениее моточасы | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10623 | IDX: null | Local HMI | DG_read_motorhours | System Tag: Off | User-defined Tag: On | LW-24 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение уровень топлива | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10364 | IDX: null | Local HMI | DG_read_fuel_level | System Tag: Off | User-defined Tag: On | LW-26 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение до ТО, ч | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10635 | IDX: null | Local HMI | DG_read_service_hours | System Tag: Off | User-defined Tag: On | LW-28 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
до ТО, дн | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10637 | IDX: null | Local HMI | DG_read_service_days | System Tag: Off | User-defined Tag: On | LW-30 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
выработано, кВт | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10629 | IDX: null | Local HMI | DG_read_generated_P | System Tag: Off | User-defined Tag: On | LW-32 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
выработано, кВар | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10631 | IDX: null | Local HMI | DG_read_generated_Q | System Tag: Off | User-defined Tag: On | LW-34 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
выработано, кВА | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10633 | IDX: null | Local HMI | DG_read_generated_S | System Tag: Off | User-defined Tag: On | LW-36 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение статуса состояния | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10605 | IDX: null | Local HMI | DG_read_unit_status | System Tag: Off | User-defined Tag: On | LW-39 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
чтение статуса режима работы | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10606 | IDX: null | Local HMI | DG_read_unit_mode | System Tag: Off | User-defined Tag: On | LW-38 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
ДГ статус регистра аварий 10539 | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10540 | IDX: null | Local HMI | DG_status_reg10539 | System Tag: Off | User-defined Tag: On | LW-54 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
ДГ статус регистра аварий 10542 | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10543 | IDX: null | Local HMI | DG_status_reg10542 | System Tag: Off | User-defined Tag: On | LW-55 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low
ДГ статус регистра аварий 10543 | 1 | 10 | 1 | 0 | MODBUS RTU | 6x | System Tag: Off | User-defined Tag: Off | 10544 | IDX: null | Local HMI | DG_status_reg10543 | System Tag: Off | User-defined Tag: On | LW-56 | IDX: null | Off | [8 empty] | Off | [7 empty] | Low